## Slide 1
Sr. | NCR Document No. | NCR Description | Corrective Action | Issue Date | Days Passed | Current Status
1 | BV-BSW-105-0000-SOA-NCR-QL-000016 | Civil (Zone A – B2 Soffit) Substandard SF3 concrete soffit finish: recurring honeycombing, surface voids, uneven texture, embedded tape/wood. | Submit separate SF-3.0 repair Method Statement; initiate trial repair mock-up using approved repair materials. | 2026-02-17 | 226 d [OVERDUE] | SF3 soffit mock-up approval pending.
2 | BV-BSW-105-0000-SOA-NCR-QL-000019 | Civil (Zone 1-B2 Wall) Defective mock-up curved wall executed with styrofoam formwork; delay in corrective action plan submission. | 3rd-party NDT structural testing completed; submit comprehensive integrity report and Code A repair MS. | 2026-04-28 | 156 d [OVERDUE] | NDT testing conducted. The test is passed, the report has been submitted on Aconex
3 | BV-BSW-105-0000-SOA-NCR-QL-000026 | Arch / Civil (Zone 2 – B1 CMU) Unauthorized blockwork construction above lintel beam level without approved builder drawings or MEP clearance. | Submitted revised elevation drawings (WF-216178) conforming to calculations (WF-200995); coordinate MEP before casting. | 2026-06-28 | 95 d [OVERDUE] | MEP team to check conflict with lintel beams.

## Slide 2
Sr. | NCR Document No. | NCR Description | Corrective Action | Issue Date | Days Passed | Current Status
4 | BV-BSW-105-0000-SOA-NCR-QL-000028 | Civil (Zone 5 L0 to L1) ACROW clearance issued without verification, causing fresh concrete slurry leak into B2 elevator shaft. | Enforce strict ACROW pre-pour physical site checks; seal formwork joints; clean elevator shaft; submit formal CAPA. | 2026-07-12 | 81 d [OVERDUE] | Typical drawings submitted currently under review on Aconex
5 | BV-BSW-105-0000-SOA-NCR-QL-000029 | Arch / MEP (Basement B2) MEP installations (HDPE hanging drainage pipes) commenced prior to architectural clearance and painting completion. | Suspend MEP works; remove HDPE pipes for painting completion; introduce mandatory Area Acceptance Record (AAR). | 2026-07-13 | 80 d [OVERDUE] | MEP proposal has been submitted to CSC, which outlines utilities can be removed in some areas and remain in other area for sofit finishing.
6 | BV-BSW-105-0000-SOA-NCR-QL-000031 | Civil (Zone 4 L0) Unauthorized cutting and drilling into completed RC structural wall for placing boom support without CSC approval. | Isolate wall; submit boom reaction calculations and opening closure MS; repair damaged rebar/concrete; hold TBT. | 2026-07-19 | 74 d [OVERDUE] | CAPA Approved (Code B) — Str calc and drwg will be submitted by 1st Oct 2026.

## Slide 3
Sr. | NCR Document No. | NCR Description | Corrective Action | Issue Date | Days Passed | Current Status
7 | BV-BSW-105-0000-SOA-NCR-QL-000032 | Architectural (Zones 2, 3, 5, 6 – B2) Repeated unauthorized bond beam casting and blockwork without approved builder drawings or MEP clearance. | Submitted updated elevation drawings (WF-220202); confirmed structural calculations (WF-200995); conduct TBT. | 2026-07-30 | 63 d [OVERDUE] | Response same as NCR-26, email to be sent
8 | BV-BSW-105-0000-SOA-NCR-QL-000033 | Architectural (Zones 9, 10, 11 – B2) Repeated failure to achieve specified SF3 fair-faced concrete finish quality: formwork misalignment, honeycombing. | Finalize comprehensive SF3 repair method statement; execute repair mock-ups for consultant inspection. | 2026-08-05 | 57 d [< 2 Months] | SF3 soffit mock-up approval pending.
9 | BV-BSW-105-0000-SOA-NCR-QL-000034 | Civil (Zone 1) Unauthorized concrete casting resulting in missing additional reinforcement around embedded steel plates in Zone 1. | Submit detailed CAPA with structural justification/NDT; work on hold at affected location until approved. | 2026-08-12 | 50 d [< 2 Months] | CAPA Approved, the closing depend on the construction schedule, expected date of closure 31st Oct.

## Slide 4
Sr. | NCR Document No. | NCR Description | Corrective Action | Issue Date | Days Passed | Current Status
10 | BV-BSW-105-0000-SOA-NCR-QL-000035 | Architectural (Zone 10-B1) Repeated unauthorized SF3 repair works on fair-faced concrete walls using unapproved cement mortar patches. | Remove unapproved cement patches; execute repairs strictly using approved MAR materials and inspected WIRs. | 2026-08-13 | 49 d [< 2 Months] | MST for SF2 & SF3 has been submitted; unauthorized patches mechanically removed.
11 | BV-BSW-105-0000-SOA-NCR-QL-000038 | Civil (Zone 2 – Wall P2-01) Unauthorized cutting and welding of structural reinforcement bars to fit embedded plates at Zone 2. | Submit structural justification, rebar repair details, and CAPA for Consultant review; hold further works. | 2026-08-20 | 42 d [< 2 Months] | Close out submitted on 29th Sep.
12 | BV-BSW-105-0000-SOA-NCR-QL-000039 | Façade (Façade Mockup) JANGHO unauthorized welding on Façade Mockup: no approved WPS, uncertified welders, non-compliant with AWS D1.1. | Suspended welding works; submit WPS, welder qualification records, calibration certificates, and Welding MS & ITP. | 2026-08-20 | 42 d [< 2 Months] | CAPA will be submitted today 1st Oct

## Slide 5
Sr. | NCR Document No. | NCR Description | Corrective Action | Issue Date | Days Passed | Current Status
13 | BV-BSW-105-0000-SOA-NCR-QL-000040 | Documentation / QA/QC KPI High Code C rate on Material Submittals (84 submittals at Code C; KPI < 70% vs mandatory 90% project requirement). | Enforce strict internal technical QA/QC review; withdraw non-applicable submittals; submit recovery plan to reach 90% KPI. | 2026-08-25 | 37 d [< 2 Months] | CAPA will be submitted
14 | BV-BSW-105-0000-SOA-NCR-QL-000042 | Civil (Zone 9 B1 Joint) Repeated non-compliance: formwork removed at construction joint at Zone 9 B1. Edge shutter stripped prematurely. | Halt premature formwork stripping; reinstate edge shutter support; inspect joint face and submit method statement. | 2026-08-27 | 35 d [< 2 Months] | CAPA approved, close-out will be submitted on 1st Oct.
15 | BV-BSW-105-0000-SOA-NCR-QL-000043 | Civil (Slab Zone 9 B1) Unacceptable concrete quality and ineffective preventive measures on slab at Zone 9 B1: surface voids and uneven finish. | Perform thorough concrete defect mapping, core testing/NDT if requested; submit remedial method statement and controls. | 2026-08-30 | 32 d [< 2 Months] | Test report has been submitted

## Slide 6
Sr. | NCR Document No. | NCR Description | Corrective Action | Issue Date | Days Passed | Current Status
16 | BV-BSW-105-0000-SOA-NCR-QL-000044 | Quality / Documentation NEW: Low NCR Closure KPI and Overdue NCRs: Issued by Client/Consultant due to slow closeout turnaround and accumulated overdue items. | Formulate and submit an immediate, high-priority NCR Recovery Plan; mobilize dedicated technical engineers to close pending items. | 2026-09-06 | 25 d [< 2 Months] | NCR closing on-going process.
17 | BV-BSW-105-0000-SOA-NCR-QL-000045 | Civil (Zone 5) NEW: Unauthorized cutting/welding of non-weldable structural reinforcement bars and unauthorized concrete demolition works in Zone 5. | Immediately cease cutting/welding & demolition in Zone 5; submit structural damage evaluation and rebar reinstatement MS. | 2026-09-06 | 25 d [< 2 Months] | CAPA has been approved, close-out expected by 7th Oct.
18 | BV-BSW-105-0000-SOA-NCR-QL-000046 | Architectural (Zone 11 B2) NEW: Persistent and uncontrolled non-compliance with SF3 fair-faced architectural concrete finish requirements at Zone 11 (B2 level). | Stop concreting in Zone 11 fair-faced elements until formwork quality and placement practices are audited; submit detailed CAPA. | 2026-09-07 | 24 d [< 2 Months] | Test is done, report is submitted, repair will be planned

## Slide 7
Sr. | NCR Document No. | NCR Description | Corrective Action | Issue Date | Days Passed | Current Status
19 | BV-BSW-105-0000-SOA-NCR-QL-000047 | Civil (Zone 1 B1) NEW: Unauthorized concrete chipping and improper concrete cover rectification works observed at Zone 1 (B1 level). | Cease unauthorized chipping; submit structural assessment, approved repair method statement, and WIR for cover rectification. | 2026-09-08 | 23 d [< 2 Months] | CAPA has been submitted
20 | BV-BSW-105-0000-SOA-NCR-QL-000048 | Civil (Zone 1 L0 to L2) NEW: Significant wall verticality deviation noted from Level L0 to L2 in Zone 1, followed by unauthorized cosmetic repair. | Conduct comprehensive 3D laser survey for verticality deviation; submit structural integrity assessment and remedial plan to CSC. | 2026-09-09 | 22 d [< 2 Months] | CAPA has been submitted

## Slide 8
Sr. | NCR Document No. | NCR Description | Corrective Action | Issue Date | Days Passed | Current Status
21 | BV-BSW-105-0000-SOA-NCR-QL-000049 | Structural (Zone 2) NEW: Lifting of Truss 1 (Left Side Stage) executed without required QAQC inspections, lifting plan approval, and CSC clearance. | Halt further steel erection; submit third-party rigging/lifting inspection records, connection inspection WIR, and CAPA. | 2026-09-10 | 21 d [< 2 Months] | Open (Awaiting CAPA) — Lifting and connection inspection records under compilation for CSC review.
22 | BV-BSW-105-0000-SOA-NCR-QL-000050 | Architectural (Zone E – B2) NEW: Wall constructed at incorrect location in Zone E (B2 level), deviating from approved architectural setting-out drawings. | Conduct setting-out survey to verify deviation; submit structural impact assessment, demolition/relocation plan, and revised shop drawings. | 2026-09-22 | 9 d [< 2 Months] | Deviation will be corrected in the plastering works